| 091-168-12-IND | AC SD 150, w/ Dual Bar Graph |
| --- | --- |

BATTERY CHARGER AND DUAL BAR GRAPH DISPLAY

A Kussmaul Auto Charge SD150 Series Model #091-168-12-IND, 50 amp high output battery charger shall be installed.   The charger shall include a front panel amp meter shall indicate output current with protective front panel and strain relief.   The unit shall be equipped with a high temperature protection circuit which shall shut down the charger and activates an alarm.  The unit shall be automatically restored when a safe temperature is reached.   A remote dual bar graph Model #091-168-002 shall be supplied.

The front panel shall be equipped with the following LED diagnostics:

a)  high voltage

b)  low voltage

c)  insufficient output

d)  battery disconnected

e)  over temperature

The charger shall have the following operational specifications:

a)  120 volts AC input at 15 amps

b)  12 volts DC output at 50 amps

c)  Dimensions of:  14” high x 9.375” wide x 9.25” deep and weighs 41 lbs.

The battery charger shall supply a ‘single battery bank’ with automatic operation and with an aluminum enclosure.   The system shall have a built-in sense circuit to check battery voltage 120 times a second; the system shall provide automatic “boost” voltage (14.25V) for rapid recovery.  After 1 hour, switches to normal float voltage (13.25V) with no overcharging.  The unit shall include front panel connections for a remote display.